## Universal
Programme Licensed to |  | EurofFirefighter | Macdonald Barnett Partners Limited, Auckland, New Zealand | [5 empty] | EuroFirefighter-2 |  |  |  | Page 2 | [6 empty] | Page 3 | [11 empty] | Page 4
License No. | 1001
FIRESYS |  | Fire Safety Engineering Programme 8-E | [9 empty] | FIRESYS UNIVERSAL MODEL - 8E |  |  | FIRESYS UNIVERSAL MODEL - 8E | [9 empty] | FIRESYS UNIVERSAL MODEL - 8E
Version No. | 2003.mbp
Programme Title |  | UNIVERSAL FIRE MODEL | [6 empty] | Copyright
FUEL SURFACE CONTROLLED
Project Title |  | Interstate Bank Fire - Los Angeles 1988 | [5 empty] | Project Ref. | Chapter 12 |  |  |  |  | Growth Phase | Assuming t^2 Growth Rate | [7 empty] | Interval | Time | Time | Time | Total | Total | Total | Mass | Energy | BFD | ISO
[14 empty] | Growth Coefficient (time to reach 1 MW) |  | t*g | = | 150 | s = | 2.5 | min |  | No. | Intervals |  |  | Mass | Mass | Energy | Release | Release | Curve | Curve
Firecell |  | Open-plan office 1410 m2 around central core (Zone 1 of 4-Zone Travelling Fire) | [11 empty] | Time to Complete Growth Phase |  |  | = | 1394.6201 | s = | 23.2437 | min
[14 empty] | Maximum Fire Intensity in Growth Phase |  |  | = | 86.4429 | MW
| THIS IS A DOUBLE T^2 MODEL THAT MAY BE EITHER VENTILATION OR FUEL SURFACE CONTROLLED MODEL | [12 empty] | Energy Released in Growth Phase |  |  | = | 40185 | MJ | [7 empty] | Released | Released | Released | Rate | Rate
[14 empty] | Mass Released in Growth Phase |  |  | = | 2009.25 | kg = | 20 | % |  |  | ti | t" | t' | M |  | E | R | Q
|  | Fuel Type |  |  | = | Wood & Plastic | [7 empty] | Time Intervals in Growth Phase |  |  | = | 139.462 | s = | 2.3244 | min |  |  | s | s | min | kg | % | MJ | kg/s | MW | C | C
|  | Ambient Heat of Combustion |  | H'n | = | 20 | MJ/kg
|  | FLED |  | ef | = | 570 | MJ/m^2 | [14 empty] | Growth Start | 0 | 0.01 | 0.01 | 0.00016667 | 0 | 0 | 0 | 0 | 0 | 20 | 20.1996
|  | Firecell Width |  | W | = | 7.5 | m | [6 empty] | Decay Phase | Assuming t^2 Decay Rate | [7 empty] | 1 | 139.462 | 139.472 | 2.3245 | 3.0143 | 0.029854 | 60.2861 | 0.043228 | 0.86455 | 20.448 | 465.7998
|  | Firecell Depth |  | D | = | 47 | m | [6 empty] | Decay Coefficient (time to reach 1 MW) |  | t*d | = | 600 | s = | 10 | min |  | 2 | 139.462 | 278.934 | 4.6489 | 18.085 | 0.17912 | 361.6996 | 0.1729 | 3.458 | 41.5534 | 565.7773
|  | Firecell Height |  | H | = | 3 | m | [6 empty] | Time to Complete Decay Phase |  |  | = | 5578.4803 | s = | 92.9747 | min |  | 3 | 139.462 | 418.396 | 6.9733 | 57.2675 | 0.56719 | 1145.3503 | 0.38901 | 7.7802 | 129.956 | 625.2136
|  | Effective Opening Width |  | w | = | 44 | m | [6 empty] | Maximum Fire Intensity in Decay Phase |  |  | = | 86.4429 | MW |  |  |  | 4 | 139.462 | 557.858 | 9.2976 | 132.6174 | 1.3135 | 2652.3483 | 0.69157 | 13.8314 | 282.8071 | 667.6555
|  | Effective Opening Height |  | h | = | 2 | m | [6 empty] | Energy Released in Decay Phase |  |  | = | 160740 | MJ |  |  |  | 5 | 139.462 | 697.32 | 11.622 | 256.1902 | 2.5374 | 5123.8036 | 1.0806 | 21.6113 | 458.9799 | 700.6909
|  | Fire Growth Coefficient (to reach 1MW) |  | t*g | = | 150 | s = | 2.5 | min |  |  |  |  | Mass Released in Growth Phase |  |  | = | 8037 | kg = | 80 | % |  | 6 | 139.462 | 836.782 | 13.9464 | 440.0413 | 4.3583 | 8800.8262 | 1.556 | 31.1202 | 620.6602 | 727.7421
|  | Fire Decay Constant (to reach 1 MW) |  | t*d | = | 600 | s = | 10 | min |  |  |  |  | Time Intervals in Decay Phase |  |  | = | 557.848 | s = | 9.2975 | min |  | 7 | 139.462 | 976.2441 | 16.2707 | 696.2263 | 6.8956 | 13924.526 | 2.1179 | 42.3579 | 747.097 | 750.6482
NOTE | User judgement is needed for selecting values of t*g and t*d. As a general rule t*d = 4 times t*g. | [21 empty] | 8 | 139.462 | 1115.7061 | 18.5951 | 1036.8007 | 10.2687 | 20736.0132 | 2.7662 | 55.3244 | 832.1307 | 770.5124
|  | Design Fire Load Mass |  | M | = | 10046.25 | kg | [6 empty] | Total Energy Released |  |  | = | 200925 | MJ |  |  |  | 9 | 139.462 | 1255.1681 | 20.9195 | 1473.8199 | 14.597 | 29476.3976 | 3.501 | 70.0199 | 878.2823 | 788.0486
|  | Design Fire Load Energy |  | E | = | 200925 | MJ | [6 empty] | Total Mass Released |  |  | = | 10046.25 | kg |  |  | Growth End | 10 | 139.462 | 1394.6301 | 23.2438 | 2019.3395 | 20 | 40386.7893 | 4.3222 | 86.4441 | 892 | 803.7458
|  | Energy at FC/VC Crossover Point |  | Etp | = | 275820.116 | MJ | [6 empty] | Total Time |  |  | = | 6973.1004 | s = | 116.2183 | min | Ventilation Start | 11 | 0.0001911 | 1394.6303 | 23.2438 | 2019.3403 | 20 | 40386.8059 | 4.3222 | 86.4441 | 892 | 803.7459
|  | Fire is Fuel or Ventilation Controlled |  |  | = | Fuel Controlled | [16 empty] | 12 | 0.0001911 | 1394.6305 | 23.2438 | 2019.3411 | 20 | 40386.8224 | 4.3222 | 86.4441 | 892 | 803.7459
|  | Firecell Area |  | Af | = | 352.5 | m^2 | [15 empty] | 13 | 0.0001911 | 1394.6307 | 23.2438 | 2019.3419 | 20 | 40386.8389 | 4.3222 | 86.4441 | 892 | 803.7459
|  | Opening Area |  | Av | = | 88 | m^2 | [15 empty] | 14 | 0.0001911 | 1394.6308 | 23.2438 | 2019.3428 | 20 | 40386.8554 | 4.3222 | 86.4441 | 892 | 803.7459
|  | Opening Ratio |  | Av/Af | = | 0.24965 | - | [15 empty] | 15 | 0.0001911 | 1394.631 | 23.2439 | 2019.3436 | 20 | 40386.8719 | 4.3222 | 86.4441 | 892 | 803.7459
|  | Ventilation Factor |  | Fv | = | 124.4508 | m^2.5 |  |  | 34.8559 | [12 empty] | 16 | 0.0001911 | 1394.6312 | 23.2439 | 2019.3444 | 20 | 40386.8885 | 4.3222 | 86.4441 | 892 | 803.746
[14 empty] | VENTILATION CONTROLLED | [8 empty] | 17 | 0.0001911 | 1394.6314 | 23.2439 | 2019.3452 | 20 | 40386.905 | 4.3222 | 86.4441 | 892 | 803.746
|  | Internal Surface Area 2 |  | At2 | = | 944 | m^2 | [6 empty] | Ventilation Limit (based on R=kp.Ah^0.5) |  | Qv | = | 106.7727 | MW |  |  |  | 18 | 0.0001911 | 1394.6316 | 23.2439 | 2019.3461 | 20 | 40386.9215 | 4.3222 | 86.4441 | 892 | 803.746
|  | Opening Factor 2 |  | Fo2 | = | 0.13183 | m^1.5 |  |  | 7.5853 | [12 empty] | 19 | 0.0001911 | 1394.6318 | 23.2439 | 2019.3469 | 20.0001 | 40386.938 | 4.3222 | 86.4441 | 892 | 803.746
|  | Pyrolisis Coefficient |  | kp | = | 0.042898 | kg/s.m^2.5 | [6 empty] | Growth Phase | Assuming t^2 Growth Rate : | [6 empty] | Ventilation End | 20 | 0.0001911 | 1394.632 | 23.2439 | 2019.3477 | 20.0001 | 40386.9545 | 4.3222 | 86.4441 | 892 | 803.746
|  | Maximum Burn Rate |  | Rmax | = | 4.3221 | kg/s | [6 empty] | Growth Coefficient (time to reach 1 MW) |  | t*g | = | 150 | s = | 2.5 | min | Decay Start | 21 | 557.848 | 1952.48 | 32.5413 | 4201.4261 | 41.6119 | 84028.5214 | 3.501 | 70.0199 | 761.7789 | 853.9307
|  | Maximum Fire Intensity |  | Qmax | = | 86.4429 | MW = | 0.24523 | MW/m^2 |  |  |  |  | Time to Reach Steady State Phase |  |  | = | 1394.6201 | s = | 23.2437 | min |  | 22 | 557.848 | 2510.3281 | 41.8388 | 5949.503 | 58.9252 | 118990.0592 | 2.7662 | 55.3244 | 552.3079 | 891.4579
[14 empty] | Maximum Fire Intensity in Growth Phase |  |  | = | 86.4429 | MW |  |  |  | 23 | 557.848 | 3068.1761 | 51.1363 | 7311.8004 | 72.4177 | 146236.0078 | 2.1179 | 42.3579 | 378.7734 | 921.4434
|  | Growth Phase Duration |  | tg | = | 1394.6201 | s = | 23.2437 | min = | 20 | % |  |  | Energy Released in Growth Phase |  |  | = | 40184.9959 | MJ |  |  |  | 24 | 557.848 | 3626.0241 | 60.4337 | 8336.5404 | 82.5669 | 166730.8072 | 1.556 | 31.1202 | 256.6295 | 946.417
|  | Steady Phase Duration |  | ts | = | 0.001911 | s = | 3.185e-05 | min = | 2.7406e-05 | % |  |  | Mass Released in Growth Phase |  |  | = | 2009.2498 | kg = | 20 | % |  | 25 | 557.848 | 4183.8722 | 69.7312 | 9071.9449 | 89.8505 | 181438.8975 | 1.0806 | 21.6113 | 175.4885 | 967.8168
|  | Decay Phase Duration |  | td | = | 5578.4803 | s = | 92.9747 | min = | 79.9999 | % |  |  | Time Intervals in Growth Phase |  |  | = | 139.462 | s |  |  |  | 26 | 557.848 | 4741.7202 | 79.0287 | 9566.2359 | 94.7461 | 191324.7187 | 0.69157 | 13.8314 | 122.6494 | 986.5386
|  | Total Fire Duration |  | t | = | 6973.1123 | s = | 116.2185 | min = | 100 | % | [11 empty] | 27 | 557.848 | 5299.5682 | 88.3261 | 9867.6355 | 97.7312 | 197352.7107 | 0.38901 | 7.7802 | 88.3572 | 1003.1787
[14 empty] | Steady State Phase | [8 empty] | 28 | 557.848 | 5857.4163 | 97.6236 | 10024.3657 | 99.2835 | 200487.3136 | 0.1729 | 3.458 | 66.0022 | 1018.1542
|  | Energy Released in Growth Phase |  | Eg | = | 40184.9959 | MJ = | 2009.2498 | kg = | 20 | % |  |  | Time to Complete Steady State Phase |  |  | = | 0.001911 | s = | 3.185e-05 | min |  | 29 | 557.848 | 6415.2643 | 106.9211 | 10084.6484 | 99.8806 | 201692.9674 | 0.043228 | 0.86455 | 51.3076 | 1031.7679
|  | Energy Released in Steady Phase |  | Es | = | 0.16519 | MJ = | 0.0082597 | kg = | 8.2217e-05 | % |  |  | Ventilation Limit |  | Qv | = | 86.4429 | MW |  |  | End of Fire | 30 | 557.848 | 6973.1123 | 116.2185 | 10096.7056 | 100 | 201934.1119 | 0 | 0 | 41.5499 | 1044.2471
|  | Energy Released in Decay Phase |  | Ed | = | 160739.8389 | MJ = | 8036.9919 | kg = | 79.9999 | % |  |  | Energy Released during Steady State Phase |  |  | = | 0.16519 | MJ |  |  |  | 1.25 |  |  | 145.2732 | 10096.7056 | 100 | 201934.1119 | 0 | 0 | 27.1932 | 1077.6489
|  | Total Energy Released |  | E | = | 200925 | MJ = | 10046.25 | kg = | 100 | % |  |  | Mass Released during Steady State Phase |  |  | = | 0.0082597 | kg = | 8.2217e-05 | % |  | 1.5 |  |  | 174.3278 | 10096.7056 | 100 | 201934.1119 | 0 | 0 | 22.6406 | 1104.9449
[14 empty] | Time Intervals in Steady State Phase |  |  | = | 0.0001911 | s =
|  | BFD Time Temperature Curve | [7 empty] | Guides
|  | Peak Temperature |  | Tp | = | 872 | C |  |  | 975.4883 |  |  |  | Decay Coefficient (time to reach 1 MW) |  | t*d | = | 600 | s = | 10 | min
|  | Peak Time |  | tp | = | 23.2437 | min | [6 empty] | Time to Complete Decay Phase |  |  | = | 5578.4803 | s = | 92.9747 | min
|  | Shape Parameter |  | sc | = | 0.7 | - |  |  | 1.5872 |  |  |  | Maximum Fire Intensity in Decay Phase |  |  | = | 86.4429 | MW
NOTE | User judgement is needed for selecting values of Tp and sc. | [12 empty] | Energy Released in Decay Phase |  |  | = | 160739.8389 | MJ
|  | Fire Fighting Water Requirements | [11 empty] | Mass Released in Decay Phase |  |  | = | 8036.9919 | kg = | 79.9999 | %
[14 empty] | Time Intervals in Decay Phase |  |  | = | 557.848 | s
|  | Heating Efficiency Factor |  | k12 | = | 0.63 | - |  |  | 0.5
|  | Cooling Efficiency Factor |  | k13 | = | 0.5 | - |  |  | 0.5
|  | Minimum Water Flow |  | F | = | 41.8112 | l/s = | 0.48369 | l/s/MW | 0.082329 | l/s/m^2
|  | Theoretical Cooling Intensity at 100 C |  | Qw | = | 108.918 | MW | [6 empty] | Total Energy Released |  |  | = | 200925 | MJ
|  | Theoretical Cooling Intensity at 600 C |  | Qw | = | 150.6456 | MW | [6 empty] | Total Mass Relased |  |  | = | 10046.25 | kg
|  | Minimum Flow Duration |  | tw | = | 34.8655 | min = | 0.58109 | hr |  |  |  |  | Total Time |  |  | = | 6973.1023 | s = | 116.2184 | min
|  | Minimum Water Storage |  | S | = | 87466.1273 | litres = | 0.43532 | l/MJ
|  | Average Discharge Density |  | dd | = | 7.1168 | mm/min
|  | Average Water Depth over Floor. |  | wd | = | 248.1309 | mm = | 248.1309 | l/m^2

## Background 1
FIRESYS PROGRAMME 8-E : UNIVERSAL FIRE MODEL | [10 empty] | Background 1 Data
General :
Programme 8-E can be used to determine how long a double t^2 design fire will last
for a given amount of fuel. The programme produces 30 sets of output data which can be
used as a "design fire". The "design fire" can then be used as input data into other fire
programmes such as BRANZFIRE, FPETOOL, FIRECALC, CFAST, etc.
Programme 8-E assumes a constantly growing or decaying fire referred to as a "t^2 fire".
The fire will stop when it reaches the limit of the fuel. The limit can be seen in the columns
for mass "M" or energy "E". The programme calculates values for "ti" and "tn" automatically.
Users can also refer to Programmes 8-B, 8-C and 8-D to obtain a general idea as to how
to how Programme 8-E works.
Select a metric fire growth rate coefficient from below or use any desired intermediate value.
The pyrolysis coefficient kp used in Programme 8-E is from Ref (2).
In some cases a "Guide Values" can be seen in grey colour on the first page.
For Fire Fighting Water Requirements refer also to Programme 10-A, particularly Background 2.
This programme may not be applicable to large firecells or large pool fires. Use discretion.
Equations :
|  | M | = | E / H'n…………………………………………………………………………….. | [6 empty] | kg
|  | Etp | = | 0.333 * (H'n * kp * Fv)^1.5 * (t*g + t*d )……………………………………… | [6 empty] | MJ
|  | Fv | = | Av * (Hv)^0.5..................………......…………………………………………. | [6 empty] | m^2.5
|  | Af | = | W * D……………………………………………………………………………… | [6 empty] | m^2
|  | Av | = | w * h………………………………………………………………………………. | [6 empty] | m^2
|  | Fv | = | w * h^1.5…………………………………………………………………………. | [6 empty] | m^2.5
|  | At2 | = | 2 * Af + 2 * (W+D) * H - Av…………………………………………………….. | [6 empty] | m^2
|  | Fo2 | = | Fv / At2.....................………….......…………………………………………. | [6 empty] | m^1.5
|  | kp | = | 1 / (148 Fo2 + 3.8)………..……………. |  |  |  | (Eq. 7, Ref 1, Law's Method)……………… |  |  | kg/s.m^2.5
|  | Rmax | = | Qmax / H'n………………………………………………………………………. | [6 empty] | kg/s
|  | Qmax | = | Least of (tg / t*g)^2 (Fuel Control) or H'n * kp * Fv (Vent Control)……. | [6 empty] | MW
|  | t | = | tg + ts + td ………………………………………………………………………… | [6 empty] | min
|  | E | = | Eg + Es + Ed…………………………………………………………………….. | [6 empty] | MJ
|  | Tp | = | ………………………………….. |  |  |  | (Eq. 3, Ref 1)………………………………… |  |  | C
|  | tp | = | tg + ts…………………………………………………………………….. |  |  |  | (Fig. 19, Ref 1)……………………………….. |  |  | min
|  | sc | = | 16 * kp…………………………. |  |  |  | (Eq. 2, Ref 1)………………………………… |  |  | -
|  | F | = | (k12 * Qmax) / (k13 * 2.605)……………………………………………. |  |  |  | …………………………………………………. |  |  | l/s
|  | Qw100 | = | 2.605 * F………………………. |  |  |  | (Fig. 10.6, Ref 2)……………………………. |  |  | MW
|  | Qw600 | = | 3.603 * F………………………. |  |  |  | (Fig. 10.6, Ref 2)……………………………. |  |  | MW
|  | tw | = | SF * tp = 1.5 * (tg + ts)………………………………………………………… | [6 empty] | min
|  | S | = | 60 * F * tw………………………………………………………………………… | [6 empty] | -
|  | dd | = | 60 * F / Af…………………………………………………………………………. | [6 empty] | mm/min
|  | wd | = | S / Af………………………………………………………………………………. | [6 empty] | m
For description of symbols, refer to front page of Programme 8-E.
Fire Growth and Decay
Select a metric "t*" value from below to suit a fire's growth t*g and decay t*d rate.
t*g or t*d
1 MW in
|  |  |  | For Instantaneous growth use |  |  |  |  | 1 | s
|  |  |  | Ultra Fast |  |  | UF |  | 75 | s
|  |  |  | Fast |  |  | F |  | 150 | s
|  |  |  | Moderate |  |  | M |  | 300 | s
|  |  |  | Slow |  |  | S |  | 600 | s
|  |  |  | Ultra Slow |  |  | US |  | 1200 | s
References :
| (1) | Barnett, C.R. - "BFD curve : a new empirical model for fire compartment temperatures",
Fire Safety Journal 17 (2002), pp 437 - 463.
| (2) | Barnett et al., "Fire Safety in Tall Buildings", McGraw-Hill., New York, 1922, Chapt 10.
| -1 | Macbar Fire Design Code, Ver 2.1, Nov 1999.
| -2 | Barnett, C R, - "Fire Compartment Sizing Design Method",
International Symposium on Fire Engineering For Building Structures and Safety,
The Institution of Engineers, Australia, Melbourne, Nov. 1989.
|  | B | = | M * ce…………………………………………………. |  |  |  |  | kg
|  | E | = | B*H'n………………………………………………….. |  |  |  |  | MJ
|  | tn | = | (3*En*1200^2/a^2)^0.333………………………….. |  |  |  |  | s
|  | ti | = | tn/20……………………………………..……………. |  |  |  |  | s
|  | Qn | = | (tn / t*g)^2...................…………………………….. |  |  |  |  | MW
|  | Rn | = | Qn / H'n.............................…………….………….. |  |  |  |  | kg/s
|  | En | = | E(n-1)+[(Q(n-1)+Qn)*(tn-t(n-1))]/2.....…………… |  |  |  |  | MJ
|  | Bn | = | B(n-1)+[(R(n-1)+Rn)*(tn-t(n-1))]/2....……………. |  |  |  |  | kg
where
|  | M | = | total mass (kg).
|  | ce | = | combustion efficiency (-).
|  | B | = | Vombustible mass (kg).
|  | H'n | = | ambient calorific value from PROGRAMME 1-A (MJ/kg).
|  | E | = | combustible energy (MJ).
|  | ti | = | time interval (s).
|  | tn | = | time at interval n (s).
|  | t*g | = | fire growth rate coefficient (-).
|  | Qn | = | intensity of fire at time tn (MW). = (a*tn/1200)^2
|  | Rn | = | mass release rate at time tn (kg/s).
|  | Bn | = | total mass released ti time tn (kg).
|  | En | = | total energy released to time tn (MJ).
18 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
28 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
29 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
30 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## Background 2
FIRESYS PROGRAMME 8-E : UNIVERSAL MODEL | [12 empty] | Background 2 Data
General
Programme 8-E is a double t^2 model.
The programme is a valuable learning tool as well as a simple design tool.
The user however has to use engineering judgement to insert t*g, t*d, Tp and sc and this
ability may be lacking in first time users.
To indicate the useful nature of the programme try reconstructing the following ten models.
Print each of them off to study the differences.
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
|  |  | Wood | Wood | Wood | Wood | Pool | Euro | Kwg | 20% | 40% | 60%
|  |  | Crib | Crib | Crib | Crib | Fire | Fire | Test | open | open | open
|  | H'n | 16 | 16 | 16 | 16 | 26.7 | 16 | 13.6 | 13 | 13 | 13
|  | W | 3 | 3 | 3 | 3 | 3 | 3 | 4.12 | 3.38 | 3.38 | 3.38
|  | D | 3 | 3 | 3 | 3 | 3 | 3 | 4.12 | 3.68 | 3.68 | 3.68
|  | ef | 400 | 400 | 400 | 400 | 50 | 800 | 637 | 700 | 779 | 779
|  | wv | 3 | 2 | 1 | 1 | 1 | 3 | 5.6 | 1.18 | 1.95 | 2.18
|  | hv | 2 | 2 | 2 | 10 | 1 | 1 | 2 | 2.18 | 2.18 | 2.92
|  | t*g | 377 | 377 | 377 | 377 | 1 | 1 | 526 | 175 | 245 | 295
|  | t*d | 377 | 377 | 377 | 377 | 1 | 215 | 245 | 47 | 54 | 47
|  | Tp | 900 | 1000 | 1100 | 1000 | 1000 | 1000 | 1100 | 1120 | 1120 | 1120
|  | sc | 1 | 1 | 1 | 1 | 1.5 | 1 | 0.45 | 1.4 | 1 | 1.4
Models 1, 2 and 3 show what happens when the opening width wv is decreased and the fire
progresses from a fuel surface controlled fire to a ventilation controlled fire.
Models 3 and 4 show what happens when the opening height hv is increased five times.
Model 5 is a hypothetical pool fire with instantaneous growth t*g and decay t*d alpha's of 1.
Model 6 illustrates the design shapes for burn rate and intensity of a hypothetical Eurocode fire,
but the Eurocode time-temp curve will be quite different from the BFD or ISO curves illustrated.
Model 7 is from an actual fire test - (Kawagoe LW Concrete Chapt 11)
Model 8 is from an actual fire test - (NFSC Test No. 19)
Model 9 is from an actual fire test - (NFSC Test No. 22)
Model 10 is from an actual fire test - (NFSC Test No. 25)
Note how poorly the ISO time temperature curve fits in most cases.